## Estimate
CSI | Trade | Description | Qty | Unit | Unit cost | Total | Low | High | Kind | Qty basis | Price source | Confidence | Finding | Sheets
01 | General Requirements | Superintendent, part-time to full-time on site through roofing, mechanical and drain-field work | 450 | HR | 92.17 | 41478.64 | 33231.46 | 49719.26 | base | 75 working days x 8 hr x about 75% site presence = 450 hr | BLS OEWS May 2025, Dallas-Fort Worth-Arlington MSA (area 0019100), public API series OEUM0019100000000<SOC><03¦06¦10> (fetched 2026-10-16) | high
01 | General Requirements | Project manager: buyout, submittals, RFIs on alternates, missing spec and M2.3, allowance tracking, closeout | 140 | HR | 110.49 | 15468.21 | 14082.24 | 22359.3 | base | About 8 hr/week over 15 weeks plus 20 hr for the RFI-heavy buyout = 140 hr | BLS OEWS May 2025, Dallas-Fort Worth-Arlington MSA (area 0019100), public API series OEUM0019100000000<SOC><03¦06¦10> (fetched 2026-10-16) | high
01 | General Requirements | General laborer: site cleanup, interior protection moves, debris handling | 120 | HR | 41.93 | 5031.85 | 4078.32 | 6545.25 | base | Allowance of about 8 hr/week over 15 weeks | BLS OEWS May 2025, Dallas-Fort Worth-Arlington MSA (area 0019100), public API series OEUM0019100000000<SOC><03¦06¦10> (fetched 2026-10-16) | high
01 | General Requirements | Building permit and plan review fee, contractor-paid | 1 | LS | 9344.25 | 9344.25 | 9344.25 | 9344.25 | base | One building permit for reroof, mechanical and site work; fee estimated at about 0.8% of construction value | Estimator allowance based on typical commercial permit fee schedules at about 0.8% of valuation | low | F19 | A1.2
01 | General Requirements | Trade permits: mechanical, plumbing, electrical | 3 | EA | 268.79 | 806.36 | 558.25 | 1519.69 | base | One each for mechanical, plumbing and electrical | City of Frisco Permit, Inspection and Miscellaneous Consolidated Fee Schedule | high | F19
01 | General Requirements | Delegated seismic anchorage design: stamped calculations and deferred submittal for new RTUs, exhaust fans and panel D | 1 | LS | 7475.4 | 7475.4 | 7475.4 | 7475.4 | base | One engineer package covering the base-bid equipment | Typical consulting fee for a small delegated seismic anchorage package of 4-10 pieces of equipment | low | F12 | M2.1, E1.0
01 | General Requirements | Survey layout of drain fields, leader routes and inverts | 1 | LS | 1868.85 | 1868.85 | 1868.85 | 1868.85 | base | One layout trip plus one as-built shot of inverts | Typical small-site construction staking fee | low |  | C2.0, C3.0
01 | General Requirements | Compaction testing of trench and drain-field backfill and asphalt patch | 1 | LS | 1868.85 | 1868.85 | 1868.85 | 1868.85 | base | About 4 test trips with nuclear gauge and reports | Typical testing lab trip charges for 4 visits | low |  | C2.0, C3.0
01 | General Requirements | Portable toilet | 4 | MO | 253.28 | 1013.12 | 806.36 | 1219.88 | base | 75 working days, about 3.5 months, rounded to 4 months | Zters: Portable toilet rental Dallas TX (construction rate $195-$235/mo, delivery ~$75) | high
01 | General Requirements | Storage container for roofing accessories, sheet metal and mechanical parts | 3 | MO | 292.57 | 877.7 | 598.57 | 1293.28 | base | Roofing and mechanical phases, about 3 months | Conexwest: Shipping container rental Dallas (20 ft $119-$139 per 4 weeks) | medium
01 | General Requirements | 30 CY roll-off dumpsters for roof tear-off, Roof D sheathing and sleepers, coping, mechanical and site debris | 13 | EA | 594.44 | 7727.66 | 6383.72 | 10079.55 | base | BUR and coverboard about 4 psf x 13,500 SF = 27 tons, plus Roof D deck about 2 tons and coping/misc about 2 tons = 31 tons / 3 tons per haul = 11 hauls, plus 2 for mechanical and site debris = 13 | Trash Daddy Dumpsters, Allen TX service page (20 yd = 2 tons incl., 30 yd = 3 tons incl., 14 days, $25/day extension) | high |  | A1.2
01 | General Requirements | Telehandler/forklift for roof loading, tear-off chutes and material staging | 4 | WK | 1993.44 | 7973.76 | 7973.76 | 7973.76 | base | Roofing duration about 6 weeks, with the machine on site about 4 weeks | Typical 6,000-lb reach forklift weekly rental with delivery | low
01 | General Requirements | Roof fall protection (warning lines, guardrail at hatch and ladder, anchors) and temporary weather protection/night seals | 1 | LS | 4360.65 | 4360.65 | 4360.65 | 4360.65 | base | One setup moved across roofs A-G during the work | Estimator allowance for warning-line system rental, temporary rail and nightly tie-in materials | low |  | A1.2
01 | General Requirements | Interior protection below roof and duct work in the occupied rec center (poly, floor protection, dust control) | 1 | LS | 1267.11 | 1267.11 | 570.2 | 2280.8 | base | Weight room, entry and drain/leader locations | BLS OEWS May 2025, Dallas-Fort Worth-Arlington MSA (area 0019100), public API series OEUM0019100000000<SOC><03¦06¦10> (fetched 2026-10-16) | low |  | M2.1
01 | General Requirements | Site barricades and temporary fence at drain-field excavations, with cones and signage in the parking lot | 1 | LS | 2491.8 | 2491.8 | 2491.8 | 2491.8 | base | Two excavations and the leader trench, with the parking lot left open to the public | Rented panel fence and cones for about 4 weeks | low |  | C2.0, C3.0
01 | General Requirements | Small tools, consumables, first aid and safety supplies | 1 | LS | 1033.8 | 1033.8 | 516.9 | 2067.6 | base | Project-wide | BLS OEWS May 2025, Dallas-Fort Worth-Arlington MSA (area 0019100), public API series OEUM0019100000000<SOC><03¦06¦10> (fetched 2026-10-16) | low
01 | General Requirements | As-builts, O&M manuals, roof warranty documents and closeout | 1 | LS | 1123.98 | 1123.98 | 561.99 | 2107.46 | base | Project closeout | BLS OEWS May 2025, Dallas-Fort Worth-Arlington MSA (area 0019100), public API series OEUM0019100000000<SOC><03¦06¦10> (fetched 2026-10-16) | medium
02 | Demolition | Demo wood privacy fence and haul off | 1 | LS | 1868.85 | 1868.85 | 1868.85 | 1868.85 | base | Fence length not dimensioned; carried as one small run near the drain field | About 2 laborers x 1 day plus haul | low |  | A1.2, C2.0
03 | Concrete | Replace 4 in concrete sidewalk with W1.4xW1.4 WWM and thickened edge | 100 | SF | 6.54 | 653.96 | 493.56 | 863.73 | base | Same area as removal, 100 SF | Staxen pricing guide: Concrete (updated 2026-10-15) | medium |  | C3.0
05 | Metals | Demo existing exterior roof access ladder | 1 | EA | 373.77 | 373.77 | 373.77 | 373.77 | base | One existing ladder per demo plan | About 6 laborer-hours with disposal | low |  | A1.2
05 | Metals | New aluminum roof access ladders with serrated rungs, wall brackets at 10 ft o.c. max, sealed fasteners | 2 | EA | 3737.7 | 7475.4 | 7475.4 | 7475.4 | base | (2) new roof ladders per details 6,7/A2.3 | Typical fixed aluminum roof ladder up to about 20 ft, furnished and installed | low |  | A2.3
05 | Metals | Steel roof hatch ladder: 1-1/4 in rungs at 12 in o.c., 2x1/4 verticals, brackets, fold-out feet bolted to floor, 2 anchors/leg | 1 | EA | 2740.98 | 2740.98 | 2740.98 | 2740.98 | base | One hatch ladder per detail | Shop-fabricated painted steel ladder about 12-14 ft, installed | low |  | A2.3
06 | Rough Carpentry | Blocking for hatch ladder brackets, with (2) 2x8 and plywood filler and 2x blocking at hatch | 40 | LF | 3.7 | 147.92 | 115.78 | 207.09 | base | Hatch framing about 4 sides x 3 ft x 2 plies = 24 LF, plus ladder bracket blocking 16 LF = 40 LF | Staxen pricing guide: Framing lumber 2026 | medium |  | A2.3
06 | Rough Carpentry | Demo roofing, sheathing and sloped 2x4 sleepers at Roof D | 1000 | SF | 2.8 | 2803.28 | 2803.28 | 2803.28 | base | Roof D not dimensioned; scaled allowance of 1,000 SF pending field measure (part of the 13,500 SF total) | Typical selective demo of deck and sleepers, labor only (disposal in dumpsters) | low | F04 | A1.2, A2.2
06 | Rough Carpentry | New 5/8 in plywood roof sheathing over existing 2x12 rafters at Roofs B and D | 2200 | SF | 2.99 | 6578.35 | 6578.35 | 6578.35 | base | Roofs B + D carried at 2,000 SF (not dimensioned) + 10% waste = 2,200 SF | 5/8 in CDX plywood installed, priced above the catalog 7/16 OSB rate for thickness and grade | low | F04 | A2.2, A2.3
06 | Rough Carpentry | Wood nailers at roof edges, curbs and drain sumps for the new insulation height | 552 | LF | 3.7 | 2041.27 | 1597.82 | 2857.78 | base | Building perimeter 2 x (139.3 + 136.7) = 552 LF used for parapet/edge length | Staxen pricing guide: Framing lumber 2026 | medium |  | A1.2, A2.3
06 | Rough Carpentry | Sister new 2x4 parapet framing to existing, with blocking as needed | 552 | LF | 11.21 | 6189.63 | 6189.63 | 6189.63 | base | Perimeter 552 LF (exterior grid 139.3 x 136.7); parapet lengths not quantified on plans | 2x4 sister studs at 16 in o.c. about 3 ft tall plus top blocking, labor and material | low |  | A2.3
06 | Rough Carpentry | New 1/2 in plywood sheathing at parapets (top and faces) | 1214 | SF | 1.87 | 2268.78 | 2268.78 | 2268.78 | base | 552 LF x about 2 SF/LF = 1,104 SF + 10% waste = 1,214 SF | 1/2 in plywood installed, comparable to the catalog OSB wall sheathing rate plus plywood premium | low |  | A2.3
06 | Finish Carpentry | Composite parapet trim, 1x10 over 1x12 (larger size carried) | 580 | LF | 19.93 | 11561.95 | 11561.95 | 11561.95 | base | 552 LF + 5% waste = 580 LF | Two composite trim boards installed, about 2x the catalog fiber-cement fascia rate | low | F23 | A2.3
06 | Rough Carpentry | Infill roof openings at removed intakes, vents, relief hoods, HRV and exhaust fan: framing, sheathing, insulation | 20 | EA | 436.06 | 8721.3 | 8721.3 | 8721.3 | base | 18 intakes/vents/relief hoods + 1 HRV + 1 exhaust fan per mechanical demo keynotes = 20 | About 4 carpenter-hours plus framing and plywood per opening | low |  | M2.1, A1.2
06 | Rough Carpentry | Exhaust doghouse at EF roof penetration (assumed wood-framed, sheathed, roofed) | 1 | EA | 4360.65 | 4360.65 | 4360.65 | 4360.65 | base | One doghouse called out on M2.1 (detail is on M2.3, not received) | Small framed doghouse about 3x3 ft with louver, roofed and flashed | low | F03 | M2.1
06 | Rough Carpentry | Allowance: replacement of deteriorated roof sheathing and framing found after tear-off | 1 | LS | 25000 | 25000 | 25000 | 25000 | allowance | Decided allowance | Owner-decided allowance amount | allowance | F05 | A2.3
07 | Roofing | Tear off existing BUR, coverboard, cant strips and tapered insulation at crickets; clean deck (existing flat insulation to remain) | 13500 | SF | 1.99 | 26911.44 | 26911.44 | 26911.44 | base | Low-slope roofs A-G: Roof F 100'-0" x 72'-8" = 7,267 SF dimensioned; remaining roofs carried at about 6,233 SF scaled from A1.2 within the 139.3 x 136.7 grid (19,042 SF), less metal roofs; total 13,500 SF subject to field verification | Typical commercial BUR tear-off labor and loading; disposal carried in dumpster line | low | F04 | A1.2, A2.2
07 | Roofing | Demo existing parapet cap flashing/coping and hardware | 552 | LF | 3.74 | 2063.21 | 2063.21 | 2063.21 | base | Perimeter 552 LF | Typical coping removal labor | low |  | A2.2, A2.3
07 | Roofing | Manufacturer-designed tapered polyiso system at 1/4 in per ft to new drains, including crickets at curbs and parapets | 14175 | SF | 4.05 | 57397.06 | 57397.06 | 57397.06 | base | 13,500 SF + 5% waste and cricket overlap = 14,175 SF | Tapered polyiso averaging about 2-3 in, adhered, typical commercial installed rate | low | F09 | A2.2, A2.3
07 | Roofing | 5/8 in coverboard at roof type R2 (Roofs B and D) | 2100 | SF | 1.99 | 4186.22 | 4186.22 | 4186.22 | base | 2,000 SF + 5% waste = 2,100 SF | 5/8 in gypsum or HD-iso coverboard, adhered | low | F02 | A2.3
07 | Roofing | 60 mil EPDM fully adhered roofing system, with splicing, lap sealant, fiber cant at drains and base flashings | 14580 | SF | 6.23 | 90826.11 | 90826.11 | 90826.11 | base | 13,500 SF + 8% for laps, base flashing turn-ups and waste = 14,580 SF | Typical fully adhered EPDM installed rate (membrane, adhesive, accessories, labor) | low | F02 | A2.2, A2.3
07 | Roofing | Wrap new membrane over top of parapet | 552 | LF | 14.95 | 8252.84 | 8252.84 | 8252.84 | base | Perimeter 552 LF | EPDM parapet wrap about 3 ft girth, adhered | low |  | A2.3
07 | Sheet Metal | New 24 ga pre-finished parapet cap flashing over continuous hold-down cleats | 580 | LF | 34.89 | 20233.42 | 20233.42 | 20233.42 | base | 552 LF + 5% laps and corners = 580 LF | Shop-formed 24 ga Kynar coping with cleats, installed | low |  | A2.3
07 | Sheet Metal | 24 ga pre-finished sidewall flashing and counterflashing, including junction with existing metal roofs | 300 | LF | 27.41 | 8222.94 | 8222.94 | 8222.94 | base | Roof-to-wall and low-slope-to-metal-roof junctions not dimensioned; carried at 300 LF | Two-piece 24 ga flashing and counterflashing with termination bar | low | F07 | A2.3, A1.3
07 | Sheet Metal | Demo and infill existing scuppers (other than Roof B) | 4 | EA | 560.65 | 2242.62 | 2242.62 | 2242.62 | base | Count not tagged; carried at 4 | Framing infill, sheathing, siding patch and flashing per scupper | low |  | A1.2
07 | Sheet Metal | New scupper at Roof B: 20 ga welded sleeve, 6 in and 12 in seam flashing, sealant | 2 | EA | 809.84 | 1619.67 | 1619.67 | 1619.67 | base | (2) new scuppers per detail 5/A2.3 | Shop-fabricated welded scupper sleeve installed and stripped in | low |  | A2.3
07 | Sheet Metal | Seamless aluminum gutter at new scuppers | 20 | LF | 11.58 | 231.55 | 175.23 | 325.42 | base | 2 scuppers x 10 LF | Homewyse: Cost to install seamless gutters (national avg, May 2026) | medium |  | A2.3
07 | Sheet Metal | Aluminum downspouts at new scuppers | 2 | EA | 169.26 | 338.51 | 225.68 | 501.5 | base | One per new scupper | Fixr: Downspout installation cost | medium |  | A2.3
07 | Roofing | New flashing at existing roof penetrations to remain (stack pipes, drawband, removable counterflashing), including lead cap removal by lead-awareness-trained workers | 20 | EA | 218.03 | 4360.65 | 4360.65 | 4360.65 | base | Penetrations not counted on plans; carried at 20 | Pre-molded EPDM pipe boot or field flashing with drawband | low | F22 | A2.3
07 | Roofing | Lead vent cap disposal/recycling | 1 | LS | 622.95 | 622.95 | 622.95 | 622.95 | base | One recycling drop-off | Handling and recycler fee | low | F22
07 | Roofing | Membrane flashing up and over new mechanical curbs (4 RTU curbs + 5 exhaust fan curbs) | 9 | EA | 560.65 | 5045.89 | 5045.89 | 5045.89 | base | RTU-2 to RTU-5 (4) + EF-1 to EF-5 (5) = 9 | Curb flashing labor and membrane per curb, detail 4/A2.3 | low |  | A2.3
07 | Roofing | Roof walkway pads from hatch to roof access ladder | 1 | LS | 1868.85 | 1868.85 | 1868.85 | 1868.85 | base | One route; about 60 LF of pads | EPDM walkway pads about $25/LF installed | low |  | A1.2
07 | Roofing | Roof hatch with curb, cant per manufacturer, membrane flashing | 1 | EA | 4734.42 | 4734.42 | 4734.42 | 4734.42 | base | One hatch per detail | Typical 30x36 galvanized roof hatch furnished and installed | low | F02 | A2.3
07 | Roofing | Hatch opening 5/8 in MDO returns, spray foam insulation and caulking | 1 | LS | 996.72 | 996.72 | 996.72 | 996.72 | base | One hatch opening | MDO trim, spray foam kit and sealant, carpenter labor | low |  | A2.3
07 | Roofing | Manufacturer warranty inspection and registration (standard warranty) | 1 | LS | 1868.85 | 1868.85 | 1868.85 | 1868.85 | base | One roof system warranty | Typical manufacturer inspection and warranty fee | low | F02
07 | Firestopping | UL-listed firestopping at rated penetrations for ducts, rain leaders and conduit | 10 | EA | 27.18 | 271.78 | 179.71 | 476.84 | base | Estimated 10 rated penetrations | The Virtual Estimation: Firestopping estimating guide (productivity per penetration / LF) | medium
09 | Finishes | Patch wall at removed weight room wall fan to match adjacent construction | 1 | EA | 1121.31 | 1121.31 | 1121.31 | 1121.31 | base | One wall fan removal (note 1) | Framing infill, sheathing, siding and interior gypsum patch with paint | low |  | M2.1
09 | Finishes | Allowance: patch and paint interior finishes affected by drain, piping and duct work, to nearest break | 1 | LS | 10000 | 10000 | 10000 | 10000 | allowance | Decided allowance | Owner-decided allowance amount | allowance | F13
22 | Plumbing | Roof drain assembly RD-1, 3 in, with sump box, clamping ring, strainer, mastic | 3 | EA | 1744.26 | 5232.78 | 5232.78 | 5232.78 | base | 3 new rain leader connections per architectural note; one drain each | Cast iron roof drain body and sump installed | low |  | A2.2, A2.3
22 | Plumbing | Overflow roof drain OD-1, 3 in, with 2 in water dam collar, strainer and clamping ring | 3 | EA | 1868.85 | 5606.55 | 5606.55 | 5606.55 | base | One overflow paired with each main drain | Cast iron overflow drain with dam collar installed | low |  | A2.3
22 | Plumbing | Interior rain leaders, no-hub cast iron (ABS only where concealed and allowed), 1 in fiberglass insulation, tested | 120 | LF | 105.9 | 12708.18 | 12708.18 | 12708.18 | base | Lengths not shown; 3 leaders x 40 LF from drain to below subfloor and out through the foundation = 120 LF | 3-4 in no-hub cast iron with hangers and 1 in insulation, installed | low | F18 | A2.2
22 | Plumbing | Overflow piping to exterior discharge, cast iron, insulated | 90 | LF | 105.9 | 9531.14 | 9531.14 | 9531.14 | base | Lengths not shown; 3 overflows x 30 LF = 90 LF | Same as rain leaders | low | F18 | A2.2
22 | Plumbing | Rain leader penetration through foundation wall with continuous sealant; floor sealing below subfloor | 3 | EA | 560.65 | 1681.96 | 1681.96 | 1681.96 | base | One per rain leader | Core or sleeve and seal per penetration | low |  | A2.2
22 | Plumbing | Overflow downspout nozzle set in sealant at siding, spray-foamed wall | 3 | EA | 436.06 | 1308.19 | 1308.19 | 1308.19 | base | One per overflow | Cast nozzle plus wall penetration and foam | low |  | A2.2
23 | HVAC | Demolish RTUs, roof curbs and appurtenances (base-bid units RTU-2 to RTU-5) | 4 | EA | 1495.08 | 5980.32 | 5980.32 | 5980.32 | base | 6 RTUs keynoted, less RTU-1 and RTU-6 in alternates = 4 | Disconnect, refrigerant recovery, cut-out and rig down per unit (crane in separate line) | low | F01 | M2.1
23 | HVAC | Demolish HRV, exhaust fan, wall fan, 18 OA intakes/roof vents/relief hoods with ductwork and appurtenances | 1 | LS | 3239.34 | 3239.34 | 3239.34 | 3239.34 | base | 1 HRV + 1 EF + 1 wall fan + 18 roof hoods per keynotes; about 60 hr of mechanic time | 60 hr x about $40.56/hr (catalog HVAC mechanic) plus disposal, rounded | low | F17 | M2.1
23 | HVAC | Demolish gas piping and supports down through roof; seal and cap | 1 | LS | 1868.85 | 1868.85 | 1868.85 | 1868.85 | base | 3/4 in and 1-1/2 in gas runs per demo plan | About 32 hr pipefitter plus caps | low |  | M2.1
23 | HVAC | Gas/electric rooftop units (Daikin) with economizer, power exhaust, CO2 sensor, low ambient controls and duct smoke detector, set and started (RTU-2 to RTU-5) | 4 | EA | 32393.4 | 129573.6 | 129573.6 | 129573.6 | base | 6 scheduled RTUs less RTU-1 (Alt #1) and RTU-6 (Alt #2) = 4 | Packaged gas/electric RTU averaging about 10 tons with listed accessories, furnished, set and started; catalog has only a 5-ton heat pump | low | F01 | M2.1
23 | HVAC | New factory roof curbs for RTU-2 to RTU-4 | 3 | EA | 1581.35 | 4744.04 | 2034.28 | 9649.11 | base | RTU-1 to RTU-4 get factory curbs; RTU-1 is in the alternate = 3 | Budget Heating: Roof curbs and adapter curbs (Daikin 3-6 ton 14 in curb $425) | medium | F08 | M2.1
23 | HVAC | Field-fabricated 24 in insulated curb with duct transition for RTU-5 | 1 | EA | 8098.35 | 8098.35 | 8098.35 | 8098.35 | base | RTU-5 and RTU-6 field curbs; RTU-6 is in the alternate = 1 | Shop-fabricated curb with transition and insulation, installed | low | F08 | M2.1
23 | HVAC | Crane service for RTU removal and setting | 4 | EA | 1447.32 | 5789.28 | 3308.16 | 10338 | base | One lift allowance per base-bid RTU (demo and set in the same pick) | RiggingForce: HVAC rooftop crane cost | high
23 | HVAC | Duct connections and modifications at new RTUs: galvanized sheet metal, 1 in internal lining at drops, 2 in duct wrap, sealing per SMACNA | 4 | EA | 4360.65 | 17442.6 | 17442.6 | 17442.6 | base | One connection package per base-bid RTU | Typical supply/return transition and connection work per RTU replacement | low |  | M2.1
23 | HVAC | Gas piping reconnection to new RTUs: black steel, cocks, unions, drip legs, supports, test | 4 | EA | 2242.62 | 8970.48 | 8970.48 | 8970.48 | base | One per base-bid RTU; routing on M2.3 not received, so reconnection near the existing locations is assumed | About 20 LF of 1-1/4 to 1-1/2 in black steel with fittings and roof supports per unit | low | F03 | M2.1
23 | HVAC | Exhaust fans EF-1 to EF-5 (Greenheck), with curbs, backdraft dampers, set and connected | 5 | EA | 3986.88 | 19934.4 | 19934.4 | 19934.4 | base | 5 scheduled fans | Roof or inline exhaust fan with factory curb, furnished and installed | low |  | M2.1
23 | HVAC | Insulated exhaust duct up through roof: (2) 8 in and (1) 10 in to doghouse | 3 | EA | 1059.02 | 3177.05 | 3177.05 | 3177.05 | base | 3 risers per plan note | About 15 LF insulated round duct with roof penetration per riser | low |  | M2.1
23 | HVAC | 12x12 exhaust grilles, Type A, 200 CFM | 2 | EA | 145.02 | 290.04 | 178.32 | 468.36 | base | 2 shown on plan | Jackson Systems: Titus TMS 24x24 ceiling diffuser, 8 in neck ($102.00) | high |  | M2.1
23 | HVAC | Surface-mounted double deflection air outlets, Titus 350RL, with flex connection (5 ft max, R-4.2) | 6 | EA | 145.02 | 870.12 | 534.96 | 1405.08 | base | Scheduled but not counted on the received plans; carried at 6 | Jackson Systems: Titus TMS 24x24 ceiling diffuser, 8 in neck ($102.00) | high | F17 | M2.1
23 | Controls | Thermostats for RTUs and temperature sensors/switches for exhaust fans, wired and configured | 7 | EA | 243.77 | 1706.42 | 1056.68 | 3086.84 | base | 4 base-bid RTUs + 3 TS for fans = 7 | JC Energy Solutions: Thermostat installation cost 2026 | high |  | M2.1
23 | HVAC | Seismic restraint hardware and curb anchorage for new RTUs and fans | 9 | EA | 560.65 | 5045.89 | 5045.89 | 5045.89 | base | 4 RTUs + 5 EFs = 9 | Seismic clips, hold-downs and fasteners per engineered design, installed | low | F12 | M2.1
23 | TAB | Independent test and balance with final report, base-bid RTUs and exhaust fans | 9 | EA | 775.35 | 6978.15 | 3256.47 | 13956.3 | base | 4 RTUs + 5 EFs = 9 systems | PickComfort: Air balance report cost (per system/AHU $150-$1,200) | medium | F15 | M2.1
26 | Electrical | Electrical demolition: roof equipment circuits on panels B and C, wall fan wiring and controls, existing panel X | 32 | HR | 57.43 | 1837.78 | 1187.4 | 2502.63 | base | About 4 days for one electrician | BLS OEWS May 2025, Dallas-Fort Worth-Arlington MSA (0019100), via BLS public API series OEUM0019100000000<SOC><type> | high |  | E1.0
26 | Electrical | New panel D replacing panel X (same rating as X assumed), set and labeled | 1 | EA | 5606.55 | 5606.55 | 5606.55 | 5606.55 | base | One panel per E1.0 | 225A-class 3-phase panelboard with breakers, installed | low | F11 | E1.0, E5.0
26 | Electrical | Reconnect existing branch circuits to new panel D | 1 | EA | 1498.96 | 1498.96 | 934.64 | 2590.38 | base | One panel changeover | Angi: Move electrical panel cost (subpanel $1,000-$3,000) | medium | F11 | E1.0
26 | Electrical | Feeder to panel D from main distribution | 50 | LF | 17.85 | 892.73 | 680.4 | 1182.38 | base | Up to 50 LF per qualification; routing not shown | Industrial Man Lifts: 1/0 copper THHN ($1.39/ft under 2,500 ft, $1.18/ft 2,500+) | medium | F11 | E1.0
26 | Electrical | New feeders and fused disconnects to RTU-2 to RTU-5 | 4 | EA | 815.53 | 3262.14 | 2157.68 | 5280.88 | base | 4 base-bid RTUs | PickHVAC: Cost to replace AC disconnect box | medium |  | E1.0, E3.0
26 | Electrical | Service receptacles at RTUs (GFCI, weatherproof) | 4 | EA | 103.95 | 415.81 | 268.73 | 931.68 | base | One per base-bid RTU | Amperio: Electrician cost per outlet 2026 | medium |  | E3.0
26 | Electrical | Final connections to exhaust fans EF-1 to EF-5 | 5 | EA | 148.18 | 740.91 | 431.7 | 1359.19 | base | 5 fans | InstaElectricians: Cost to install a dedicated circuit 2026 | medium |  | E3.0
26 | Electrical | Heat trace cable on rain leaders, overflows and site DIP leader (electrical only, once) | 187 | LF | 34.89 | 6523.53 | 6523.53 | 6523.53 | base | Site DIP 80 LF + overflow piping 90 LF = 170 LF + 10% for drain bodies and fittings = 187 LF | Self-regulating heat trace installed with fittings and labels | low | F14 | E3.0, E4.0, C3.0
26 | Electrical | Heat trace controller, GFEP breaker and dedicated circuit (HT RUN #1) | 1 | LS | 3114.75 | 3114.75 | 3114.75 | 3114.75 | base | One heat trace control system | Ambient-sensing controller, contactor, GFEP breaker and about 75 LF of branch circuit | low | F14 | E4.0
28 | Fire Alarm | Remote audio/visual duct detector alarm at main check-in counter, one per RTU with a duct detector | 4 | EA | 560.65 | 2242.62 | 2242.62 | 2242.62 | base | 4 base-bid RTUs, each assumed to carry a duct detector | Remote alarm/test station with wiring | low | F21 | M2.1, E3.0
26 | Electrical | Allowance: trace and verify panel C feed | 1 | LS | 5000 | 5000 | 5000 | 5000 | allowance | Decided allowance | Owner-decided allowance amount | allowance | F16 | E1.0
31 | Earthwork | Coarse washed drain rock around and over laterals, 3'-6" deep | 58 | CY | 93.44 | 5419.66 | 5419.66 | 5419.66 | base | Field 1: 30x15x3.5 = 1,575 CF less 90 LF 24 in pipe (283 CF) = 1,292 CF. Field 2: 12x4x3.5 = 168 CF less 31 CF = 137 CF. Total 1,429 CF = 53 CY + 10% compaction/waste = 58 CY | Washed drain rock delivered and placed | low |  | C2.0, C3.0
31 | Earthwork | Typar 3401 geotextile on top of drain rock | 548 | SF | 0.56 | 307.24 | 307.24 | 307.24 | base | 450 + 48 SF field areas = 498 SF + 10% laps = 548 SF | Nonwoven geotextile placed | low |  | C2.0, C3.0
31 | Earthwork | Load and haul excess spoil off site | 100 | CY | 24.92 | 2491.8 | 2491.8 | 2491.8 | base | About 80 bank CY displaced x 1.25 swell = 100 loose CY | Truck haul and dump fee per loose CY | low
31 | Earthwork | Allowance: repair or relocation of unmarked utilities encountered | 1 | LS | 15000 | 15000 | 15000 | 15000 | allowance | Decided allowance | Owner-decided allowance amount | allowance | F06 | C2.0, C3.0
32 | Landscape | Regrade disturbed area, 4 in topsoil and seeding | 1500 | SF | 1.56 | 2336.06 | 2336.06 | 2336.06 | base | Field 1 excavation top 45x30 = 1,350 SF + 10% disturbance = 1,500 SF | Fine grade, 4 in imported topsoil and hydroseed/hand seed | low |  | C2.0
33 | Site Utilities | 24 in ADS N-12 perforated CPEP laterals | 100 | LF | 59.8 | 5980.32 | 5980.32 | 5980.32 | base | Field 1: 3 x 30 = 90 LF + Field 2: 10 LF = 100 LF | 24 in N-12 perforated pipe set in rock bed, material and labor | low |  | C2.0, C3.0
33 | Site Utilities | 24 in ADS fittings: 2 perforated tees, 1 cross tee, 6 split end caps, 2 24x4 reducers, 4 split couplings | 1 | LS | 4709.5 | 4709.5 | 4709.5 | 4709.5 | base | 2 x $650 + $900 + 6 x $120 + 2 x $250 + 4 x $90 = $3,780 | Supplier-level fitting prices plus install | low |  | C2.0, C3.0
33 | Site Utilities | 4 in SCH40 ABS monitoring risers with Fernco Qwikseal, plug and 18 in VB adjustable sleeve | 3 | EA | 560.65 | 1681.96 | 1681.96 | 1681.96 | base | (3) per C2.0 | Riser, valve box and fittings installed | low |  | C2.0
33 | Site Utilities | 4 in DIP cleanout assembly: MJ wye, 45 deg MJxPE bends, DIP riser, (2) Megalug restraints | 1 | EA | 2242.62 | 2242.62 | 2242.62 | 2242.62 | base | One assembly per C3.0 detail | Ductile fittings, restraints and riser installed | low |  | C3.0

## Summary
Direct Cost | 723497.76
Allowances | 55000
Sales Tax | 0
Contingency | 72349.78
Overhead | 75725.43
Profit | 92657.3
Total | 1019230.27
Range Low | 982134
Range High | 1082905
Per SF

## Quantities
Quantity | Value | Unit | Source | Confidence | Note
roof_framing | unknown |  | E3.0 dimension strings (two readers) | medium
exterior_wall_stud | unknown |  | E3.0 dimension strings (two readers) | medium
interior_wall_stud | unknown |  | E3.0 dimension strings (two readers) | medium
foundation_type | unknown |  | E3.0 dimension strings (two readers) | medium
overall_length_ft | 139.3 | FT | A1.2 dimension strings (two readers) | medium
overall_width_ft | 136.7 | FT | A1.2 dimension strings (two readers) | medium
roof_pitches | ["1/8\" per 12\"", "1/4\" per 12\" tapered"] |  | A1.2 dimension strings (two readers) | medium

## Findings
# | Title | Severity | Sheets | Detail | Treatment | Exposure low | Exposure high | RFI | Verified
F01 | Additive Alternate #1 and #2 boundaries undefined and possibly inconsistent between trades | high | A1.1, A1.2, M1.2, E2.0, E3.0 | Alternates #1 (RTU-1 area) and #2 (RTU-6 area) are shown only as dashed boxes on the roof, mechanical and electrical sheets. No written scope, bid form line or description says whether roofing, curbs, gas piping, electrical feeders and the units themselves sit inside the alternates. The electrical demolition sheet appears to tie Alternate #2 to MAU-4, while the other sheets tie it to RTU-6. RTU-6 is a 20-ton unit on a 125 A circuit, so a misplaced boundary moves a large amount of money between the base bid and the alternate. | rfi | 40000 | 200000 | Please provide a written description of Additive Alternates #1 and #2, including the units, curbs, gas piping, feeders and roofing in each. Please also confirm whether E2.0 Alternate #2 refers to MAU-4 or RTU-6. | confirmed
F02 | Roof system, insulation and products deferred to a specification not in the bid documents | high | A2.1, A2.2, A2.3, A3.1 | The roof system, insulation R-value and thickness, hatch, drains, curbs and ladder bracket all point to a specification. Only the mechanical sheet specifications were received. Detail R1 names EPDM fully adhered over existing sheathing, but the R2 insulation has no type or thickness, and no warranty term is stated. | rfi | 30000 | 90000 | Please issue the project manual or roofing specification, including membrane thickness, insulation R-value, warranty term, roof hatch, roof drain and curb products. | confirmed
F03 | Indexed sheet M2.3 (mechanical remodel roof plan) not received; doghouse detail lives there | high | T1.1, M2.1 | The index lists M2.3 but it was not received. M2.1 points to detail 2 on M2.3 for the exhaust doghouse. Without M2.3 there is no plan for the new RTU locations, curbs, new roof penetrations, new gas piping routing or the doghouse construction. | rfi | 15000 | 60000 | Sheet M2.3 MECHANICAL REMODEL ROOF PLAN is listed in the index and referenced from M2.1 (detail 2, doghouse) but was not in the bid documents. Please issue it. | confirmed
F04 | Roof areas not dimensioned and must be field verified | high | A1.1, A1.2, A1.3 | Only the overall grid dimensions (139'-4" by 136'-8") and Roof F (100'-0" x 72'-8") are given. The demolition roof plan is NTS. Areas of Roofs A through H must be scaled from the graphic scale on A1.2 and are subject to field verification. | proceed | 20000 | 60000 | Please provide the square footage of each roof area (A–H) in the contract. | confirmed
F05 | Deteriorated deck and sheathing replacement left open with no unit price | high | A1.1, A2.3, A2.1 | Roof type R1 reuses the existing 1/2" sheathing, and the parapets keep their existing framing. Any rot found after tear-off is to be verified with the architect, but no allowance or unit price is defined. | allowance | 15000 | 60000 | Please confirm whether the owner will accept a deck replacement allowance and unit price for deteriorated sheathing found after tear-off. | confirmed
F06 | Unknown buried utilities at roof drain fields carried at no added cost | high | C1.0 | The civil notes state that existing utilities are unknown, and they shift all locating and working-around cost to the contractor. The drain fields are deep excavations (4' min cover) next to the building and under pavement. | allowance | 10000 | 40000 | Is any record of existing utilities available for the drain field areas? Will the owner accept an allowance for unmarked utilities in lieu of the no-added-cost clause? | confirmed
F07 | Metal roof exclusion conflicts with photo keynotes; Roof C not located | medium | A1.3, A1.1, A1.2 | The metal roofs are excluded, but the reference photos of Roof H carry the replace-roofing keynote. Roof C appears in a photo but is not labeled on the reference plan. The limits of the excluded metal roofs and the tie-in flashing at their edges are shown only by hatching. | rfi | 10000 | 50000 | The A1.3 photos show Roof H with the replace-roofing keynote, yet metal roofs are noted as not in contract. Is Roof H in scope? Where is Roof C on the plan? | confirmed
F08 | RTU curb type conflicts: factory curb vs field-fabricated 24" insulated curb | medium | M0.1 | Schedule notes call for factory curbs, with RTU-5 and RTU-6 sent to a field-fabricated insulated curb with duct transition. RTU-1 and RTU-2 omit notes 1 and 4, so it is unclear whether they get the economizer, smoke detector and new curbs or reuse existing ones. Curb heights also drive the roofing and flashing work. | rfi | 10000 | 40000 | Please confirm the curb type for each RTU, and whether RTU-1 and RTU-2 receive the economizer, power exhaust and duct smoke detector given in notes 1 and 4. | confirmed
F09 | Tapered insulation and cricket extents not laid out | medium | A1.2, A2.1, A2.3 | The existing roof is noted at 1/8" per 12". The new note calls for 1/4" per 12" tapered insulation to the drains, and that note text is garbled. There is no tapered layout showing starting thickness, drain sumps or cricket sizes, so the board volume cannot be confirmed. | proceed | 10000 | 30000 | Is a full 1/4" per 12" tapered system required on all reroofed areas, or only crickets and sumps? Please provide the minimum insulation thickness at the drains. | confirmed
F11 | New panel D has no rating; feeder lengths not shown | medium | E1.0, E4.0, E5.0 | Panel D replaces panel X, but E1.0 gives no amperage, bus or feeder size. E4.0 is titled for schedules but carries no panel schedules. The schedule on E5.0 must be checked to confirm it covers panel D. Feeder routing and lengths are not shown. | rfi | 8000 | 20000 | Please provide the panel D rating, main breaker or MLO, circuit count and feeder size, and confirm which schedule on E5.0 applies to panel D. | confirmed
F12 | Delegated seismic design and conflicting code editions | medium | M0.2, E4.0, T1.1 | The contractor must hire an engineer for stamped seismic anchorage of the RTUs and other equipment in a high-seismic region. The electrical notes cite the 2009 IBC, while the cover cites the latest adopted edition. No structural sheets confirm that the existing framing carries the new, heavier units. | proceed | 5000 | 20000 | Has the existing roof framing been checked for the new RTU weights? Which IBC edition governs seismic bracing? | confirmed
F13 | Interior finish repair and patch-to-match is open-ended | medium | A1.1, A2.2, M0.2, M1.1 | New drains, rain leaders, the wall fan removal and duct changes require interior ceiling and wall patching to match existing. No extent is given. The mechanical spec puts painting by others, which in a GC bid falls to us. | allowance | 5000 | 20000 |  | confirmed
F14 | Heat trace assigned by three disciplines with no length | medium | C1.0, M2.2, E3.0, E4.0 | Civil, mechanical and electrical each tell their trade to provide heat trace. Only the electrical sheet gives a partial length, and the HT RUN #1 diagram has no cable length. There is a risk of both double pricing and a gap between subs. | proceed | 5000 | 15000 | Please confirm that the E3.0 lengths govern for heat trace, and the total traced length per leader from the dry well to 3 feet above grade. | confirmed
F15 | Independent air balancing: unclear who contracts and pays | medium | M0.2 | Test and balance is required for six RTUs and the exhaust fans. The note does not say whether the owner or the contractor hires the balancer. | proceed | 8000 | 15000 | Is the independent air balancer contracted by the owner or by the contractor? | confirmed
F16 | Panel C feed assumed; junction box not found | medium | E4.0 | The engineer could not confirm how panel C is fed. Demolished roof loads are on panels B and C. If the assumption is wrong, tracing and feeder rework will be needed. | allowance | 3000 | 15000 | If the panel B to panel C tap cannot be found, what is the intended scope? | confirmed
F17 | Mechanical demolition plan has only one keynote | medium | M1.1, M1.2 | The first floor demolition plan shows ductwork and flex drops but keynotes only the wall fan, and there is no legend for existing-to-remain versus demolish. The roof demolition leaves vent quantities as necessary. | rfi | 3000 | 10000 | On M1.1, are the ducts and four flex drops with diffusers to be removed or to remain? | confirmed
F18 | Rain leader material left as cast iron or ABS | low | M0.2, M2.2 | The spec allows either material, but ABS is not allowed exposed or in return plenums. Subs may price ABS throughout. | proceed | 3000 | 10000 |  | confirmed
F19 | Utility connection charges and permit fees on contractor | low | M0.2, E4.0 | The contractor pays permits and any utility charges. If gas service or meter capacity must increase for the new RTU heating loads, those charges fall to the contractor. | proceed | 2000 | 10000 | Has the existing gas service been confirmed adequate for the new RTU heating loads? | confirmed
F20 | Broad complete-and-functioning and most-stringent clauses | low | T1.1, E4.0 | The general notes push undefined scope to the contractor through diagrammatic details and complete-system language. Combined with the missing spec and M2.3, these clauses widen exposure. | proceed | 0 | 10000 |  | confirmed
F21 | Duct smoke detector alarm quantity unclear | low | E3.0, M0.1 | Several RTUs are tagged for an audio/visual alarm at the check-in counter. It is unclear whether one shared annunciator or one per unit is required, and the product is listed only as one solution. | proceed | 2000 | 8000 |  | confirmed
F22 | Lead-capped vents require trained removal | low | A1.1 | The number of lead-capped vents is unknown. Workers need lead awareness training, and the lead must be disposed of or recycled properly. | proceed | 1000 | 5000 |  | confirmed
F23 | Parapet trim sizes differ between details | low | A2.2 | Details 2 and 6 show different composite trim sizes at the parapet (1x8 over 1x10 versus 1x10 over 1x12). The parapet lengths are not quantified. | proceed | 1000 | 3000 |  | confirmed
F24 | Reference plan numbered A1.3 but indexed as A1.0 | low | T1.1, A1.3 | The index lists A1.0 REFERENCE PLAN AND NOTES, and the sheet received with that title is numbered A1.3. This appears to be a numbering error rather than a missing sheet, but callouts to A1.0 or A1.3 should be checked. | proceed | 0 | 2000 | Please confirm that A1.3 is the sheet indexed as A1.0 and that no separate A1.0 exists. | confirmed